Text consolidated by Valsts valodas centrs (State Language Centre) with amending regulations of:

5 July 2011 [shall come into force on 1 January 2012] Not yet in force.

If a whole or part of a paragraph has been amended, the date of the amending regulation appears in square brackets at the end of the paragraph. If a whole paragraph or sub-paragraph has been deleted, the date of the deletion appears in square brackets beside the deleted paragraph or sub-paragraph.

Republic of Latvia

Cabinet

Regulation No. 498

Adopted 28 June 2011

### Regulations Regarding Latvian Construction Standard 
LBN 201-10 “Fire Safety of Structures”

Issued pursuant to Section 2,

Paragraph four of the Construction Law

1. This Regulation approves the Latvian Construction Standard LBN 201-10 “Fire Safety of Structures” (hereinafter – Construction Standard LBN 201-10).

2. According to the recommendation of the Ministry of Economics and the Ministry of Interior the limited liability company Standardisation, Accreditation and Metrology Centre shall publish the list of national standards of Latvia which are to be applied for the fulfilment of the Construction Standard LBN 201-10 on the internet site www.lvs.lv.

3. The requirements of the Construction Standard LBN 201-10 at the places of imprisonment, short-term detention facilities, institutions of social services, medical treatment institutions and in other structures, where the competent authorities have restricted the freedom of movement of persons, shall be applied insofar as it is not in contradiction with the requirements of the regulatory enactments regulating the operation of such institutions which are connected with the deprivation of liberty and with limited rights of a person to move freely.

4. Reaction to fire classes for construction products shall be determined in accordance with Table 4 of Annex to the Construction Standard LBN 201-10.

5. Cabinet Regulation No. 866 of 11 December 2007, Regulations Regarding Latvian Construction Standard LNB 201-07 “Fire Safety of Structures” (Latvijas Vēstnesis, 2007, No. 203) is repealed.

6. Building designs, which have been accepted in accordance with the specified procedures or submitted for acceptance until 31 December 2011 and the technical solutions of which comply with the requirements of regulatory enactments in force in the relevant period of time, need not to be revised in compliance with the requirements of the Construction Standard LBN 201-10. Building designs which have been developed on the basis of planning and architectural orders issued until 31 December 2011 need not to be revised in accordance with the requirements of this Regulation.

7. This Regulation shall come into force on 1 January 2012.

Prime Minister 			V. Dombrovskis

Minister for Economics 		A. Kampars

Approved by

Cabinet Regulation

No. 498

of 28 June 2011

#### Latvian Construction Standard LBN 201-10 “Fire Safety of Structures”

1. General Provisions

1. Construction Standard determines the minimum fire safety requirements to be observed when designing and building new structures, the structures to renovated, reconstructed and restored and structural elements thereof. The requirements of the Construction Standard shall apply to the structures referred to in Paragraph 5 of this Construction Standard.

2. The following terms are used in this Construction Standard:

2.1. protected escape route – a room, separated by a fire-resistant structure, without fire load and intended for evacuation of people;

2.2. open structure – a structure in the walls of each storey of which at least 30% of openings around the entire perimeter of the structure are opened and the area of aperture thereof is at least 10% of the area of the floor of the storey;

2.3. open stairs – internal stairs of a structure which are not separated from the construction volume of the structure with fire-proof boundary structures;

2.4. openable opening – window, door, gate or manhole which can be opened in the external delimiting structure of the building which can be reached with technical means of the fire and rescue service and which may be used for rescue works;

2.5. automatic firefighting water curtain, automatic water cooling system for firefighting – a fixed engineering system which upon detecting fire or upon receipt of control signal from other automatic fire protection system, which has detected the fire, ensures limitation of the spread of the fire or fire protection of the building structures;

2.6. automatic fire detection and alarm system – a fixed engineering system which automatically detects fire and transmits a signal regarding the fire or system damages to the control and indicating equipment, in case of fire switches on an alarm signal alerting devices in the structure to be protected, as well as develops signals for control of other engineering systems;

2.7. automatic voice fire alerting system – a fixed engineering system which upon receipt of control signals from another automatic fire protection system, which has detected the fire, transmits automatically a voice notification regarding the fire in the structure to be protected;

2.8. automatic smoke exhaust system – a fixed engineering system which, in case of fire, upon receipt of control signal from another automatic fire protection system, which has detected the fire, ensures exhaust of smoke from a room to be protected out of the structure, producing natural or mechanical traction of smoke in the premises to be protected;

2.9. automatic air overpressure system – a fixed engineering system which, in case of fire, upon receipt of control signal from another automatic fire protection system which has detected the fire, ensures protection of a room to be protected from filling with smoke, providing air pressure therein which exceeds air pressure in the adjacent premises;

2.10. automatic firefighting system – a fixed engineering system which upon detection of the fire or upon receipt of control signal from another automatic fire protection system, which has detected the fire, performs fire extinguishing or localisation of the fire automatically, as well as develops signals for control of other engineering systems;

2.11. autonomous fire detector – a local fire detector (device) which reacts to fire factors (concentration of smoke, high temperature) and notifies the persons who are located in a room where it is installed by sound signal and visual signalling regarding the fire. Autonomous electric power source and fire detection, light signalling, sound announcement components shall be constructively combined in the case of autonomous fire detector;

2.12. external escape stairway – stairs outside a structure or in an open environment separated with fire-resistant building structures;

2.13. floor level of the highest storey of the structure – difference between the level of a road or similar surface on which the technical means of firefighting and rescue may drive and park and the floor level of the highest storey of the structure on which the users of the structure may be present;

2.14. fire stability level of a structure – an integrated indicator of fire safety of a structure which includes type of use of the structure, floor level of the highest storey of the structure, the area of fire compartment, fire load and explosion hazard of technological processes occurring in the structure and which is characterised by fire resistance of building structures and reaction to fire of built-in construction products;

2.15. smoke-protected stairway – fire protected stairway where the possibility of smoke is not allowed;

2.16. smoke exhaust openings – doors, gates, windows to be opened or broken, blinds and manholes to be opened, open openings in external boundary structures through which it is possible to discharge smoke in case of fire;

2.17. evacuation – movement of persons to a safe place outside a structure on the level of ground surface in case of fire or other danger;

2.18. length of escape route – distance from a part of the structure or the most remote place of fire compartment along the shortest possible way up to the nearest emergency exit;

2.19. escape route – safe and easy to find path for movement which starts at any point of the structure and leads to an emergency exit;

2.20. emergency exit – exit from a structure or parts of fire compartment through which it is possible to get outside the structure on the level of ground surface;

2.21. roof covering system – roof surface and insulating structure which includes all layers which form atmosphere resistant roof structure, except bearing structure – heat insulation, steam insulation, mechanically fixed or glued roof covering (water proof), as well as additional elements – roof windows;

2.22. roof covering – the upper hydroinsulating layer of roof which protects the structure from external impact of atmosphere;

2.23. non-automatic smoke exhaust system – a fixed engineering system which, in case of manual initiation of operation, ensures exhaust of smoke from a room to be protected out of the structure, producing natural or mechanical traction of smoke in the premises to be protected;

2.24. non-ventilating facade – a multilayer structure of facade (external wall) between individual layers of which there is no air interlayer;

2.25. flat roof – delimiting structure of a structure which performs the functions of the covering of the upper storey and roof at the same time;

2.26. explosive room – a room or a group of rooms where the industrial or storage technology used forms explosive environment;

2.27. fire protected staircase – a staircase without fire load, which is separated from other premises with fire-safe structures and which has a direct exit to outside on the level of ground surface or through a lobby;

2.28. fire-resistant building structure – a building structure with standardised fire resistance limit which is intended for limitation of dangerous factors of fire;

2.29. a room, separated by a fire-resistant structure – a room which is separated from other premises with fire-resistant building structures;

2.30. area of fire compartment – area of the storey of fire compartment between external walls or external and fire walls;

2.31. fire compartment – a part of the structure which is separated from other parts of the structure with fire-safe structures so as smoke and spread of smoke is delayed to and from that part of the structure for a certain period of time;

2.32. fire-proof lobby – a room without fire load separated with fire-resistant building structures between two fire compartments or a room, separated by a fire-resistant structures;

2.33. fire resistance – the ability of building structures or elements to retain loadbearing capacity, thermal insulation and integrity for a certain period of time;

2.34. fire separation elements – building structures for the prevention of flame spread, which are made of construction products the reaction to fire class of which is at least A2-s1,d0

2.35. reaction to fire – reaction of a construction product, exposing it to fire under certain circumstances, which characterises its ability to facilitate flame spread by degradation thereof;

2.36. fire load – the amount of thermal energy (MJ) to be released during combustion process from the combustible substances, materials and devices (except construction products forming building structure) present in a room on an area unit of the floor of a room (m2);

2.37. ventilating (suspended) facade – facade structure which has an air interlayer between heat insulation and external finishing; and

2.38. lightning protection system – a uniform system which is intended for the protection of structures, certain parts thereof, electric appliances and other objects against direct and indirect influence of lightning discharge.

3. Renovation, reconstruction and restoration of a structure shall not reduce the fire safety of the structure.

4. If it is not possible to observe the minimum fire safety requirements specified in this Construction Standard in the cases specified in Section 16, Paragraph three of the Construction Law, the deviations from the technical requirements may be substantiated by calculations or the compliance of the structure with the minimum fire safety requirements specified in this Construction Standard may be proved in another way, taking into account the constructive and planning solution of the structure, functional significance and possible variants for the course of fire.

2. Fire Safety Parameters of Structures

2.1. Types of the Use of Structures

5. Depending on the requirements set for fire safety there are seven types of use of structures:

5.1. type of use I – residential buildings and premises, including few-storey one-apartment and multi-apartment residential buildings, multi-storey multi-apartment buildings, household buildings and structures, summer cottages, garden-houses, semi-detached houses, row houses;

5.2. type of use II – buildings and structures of public nature, which are intended for accommodation of people, including hotels, official accommodation facilities, hostels, motels, guest houses, shelters, sanatoriums, camp sites, recreation bases, recreation camps, other recreation buildings, barracks, other accommodation buildings (also short-term accommodation buildings);

5.3. type of use III – buildings and structures of public nature, which are used all twenty-four hours and where users to be cared for and isolated are staying, including hospitals, nursing homes, care buildings, orphanages, birthing centres, social rehabilitation centres, buildings where persons are accommodated for whom the competent authorities have limited freedom of movement;

5.4. type of use IV – buildings and structures of public nature, which are used for commercial activity and public measures including theatres, cinemas, concert halls, circuses, restaurants, cafes, bars and other public catering enterprises, stores, trade centres, market pavilions and other trade structures, conference and exhibition premises and structures, clubs, culture houses, museums, cult buildings and structures, dance halls, discotheques, libraries, court buildings, post and communication buildings and structures, railway stations, airports, bus terminals, sports structures, buildings where outpatient medical aid is provided;

5.5. type of use IVa – buildings and structures intended for educational activity, including buildings of pre-school educational institutions for children, learning buildings of elementary schools and gymnasiums, learning buildings of craft schools;

5.6. type of use V – structures which usually are used during the day and where users familiar with the premises are staying permanently, including administrative buildings, archives, banks, office buildings, buildings and structures of rescue services, learning buildings of universities and institutions of higher education, learning buildings of interest schools, buildings of other educational and scientific institutions;

5.7. type of use VI – production buildings and premises where production processes take place, and warehouses; and

5.8. type of use VII – garages and parking lots, including built-in underground and surface parking lots.

2.2. Fire Stability Levels of Structures

6. Structures have the following fire stability levels:

6.1. U1, which has two fireproofness sublevels – U1a and U1b;

6.2. U2, which has two fireproofness sublevels – U2a and U2b;

6.3. U3 – the requirements have not been determined for bearing structures of a structure in the field of fire safety and the safety level of such structures is ensured by limiting the dimensions of structures in compliance with the type of use of the structure.

7. The minimum fire resistance of building structures determined for the structure of the relevant fire stability level and minimum reaction to fire class of construction products is specified in Tables 1 and 2 of Annex to this Construction Standard.

8. Different parts of one structure may have different fire stability levels and fireproofness sublevels. The possibility of flame spread between the parts of the structure of different fire stability levels shall be eliminated by fire-proof boundary structures.

2.3. Fire Resistance of Building Structures

9. Fire resistance of structures shall be determined in compliance with the stability of loadbearing capacity (symbol R), integrity (symbol E) and thermal insulation properties of building structures during fire. Fire resistance of building structures shall be determined by testing, calculations or combining testing with calculations.

10. In addition to the fire resistance indicators referred to in Paragraph 9 of this Construction Standard the following indicators of fire resistance and smoke non-permeability shall be applied:

10.1. heat radiation limitation (symbol W);

10.2. mechanical action (symbol M);

10.3. the self-closing ability for doors, gates, windows, manholes, blinds, valves and fire-proof curtains (symbol C);

10.4. smoke leakage limitation (symbol S);

10.5. soot fire resistance (symbol G);

10.6. fire protection ability – ability of construction products to be used for covering to protect the structure behind them from ignition and charring (symbol K);

10.7. stability in constant temperature (symbol D);

10.8. stability under standard temperature/time curve conditions (symbol DH);

10.9. functionality of electric ventilators for smoke and heat exhaust (symbol F); and

10.10. functionality of the device for natural smoke and heat exhaust (symbol B).

11. The numerical indicator of the symbols referred to in Paragraphs 9 and 10 of this Construction Standard, which characterises fire resistance of bearing structures and structures forming fire compartment structure, shall be specified as minimum time in minutes of fire resistance of all parameters characterising fire resistance of the structure. If bearing structures of the structure have different times of fire resistance for integrity (symbol E), thermal insulation (symbol I) and loadbearing capacity (symbol R), the lower ensured time of fire resistance for integrity, thermal insulation and loadbearing capacity shall be specified in the numerical designation of fire safety of the structure.

12. Fire resistance shall be expressed in minutes. There are the following standard fire resistance times: 15, 30, 45, 60, 90, 120, 180 and 240 minutes.

13. Fire resistance necessary for bearing structures and building structures forming fire compartment structure shall be determined, taking into account the type of use of the structure, necessary fire stability level of the structure, floor level of the highest storey of the structure, permissible area of fire compartment and fire load of the structure or parts thereof.

14. Any building structure shall ensure the higher fire resistance time specified for the relevant building structure from the fire resistance indicators stipulated respectively. Fire resistance requirements for bearing structures and fire compartment structures are specified in Table 1 of Annex to this Construction Standard.

15. Fire resistance of fire doors shall be classified in compliance with the standard LVS EN 14600:2007 “Doorsets and openable windows with fire resisting and/or smoke control characteristics. Requirements and classification.”

16. Fire resistance of fire resistant glass shall be classified in compliance with the standard LVS EN 357:2007 “Glass in building. Fire resistant glazed elements with transparent or translucent glass products. Classification of fire resistance.”

2.4. Reaction to Fire

17. Reaction to fire of construction products is characterised by the following properties which express themselves upon a construction product getting in contact with fire:

17.1. ignition;

17.2. heat release;

17.3. flame spread;

17.4. release of smoke; and

17.5. release of burning (hot) droplets.

18. Construction products and structural elements (except floor and roof coverings, heat insulation products of pipelines) have the following reaction to fire classes:

18.1. A1 – a construction product does not react to the influence of fire, the construction products of this class do not promote development of fire in case of flash-over;

18.2. A2 – a construction product, which is exposed to the influence of fire, releases smoke in small amount, in case of flash-over it does not cause fire load and promote development of fire;

18.3. B – a construction product does not cause situations of flash-over, but it may maintain burning in case of developed fire;

18.4. C – a construction product may cause a situation of flash-over, but not at the beginning of the development of fire;

18.5. D – a construction product may cause a situation of flash-over due to influence of fire and it actively engages in the burning process when it is exposed to influence of fire;

18.6. E – a construction product may cause a situation of flash-over already in the first two minutes during burning; and

18.7. F – fire resistance limit and reaction to fire class is not specified for a construction product and it may burn fast and cause flash-over quickly.

19. The intensity of release of smoke and burning droplets of construction products and structural elements shall be designated with the following symbols:

19.1. s1 – formation of smoke is very small during reaction to fire of a construction product;

19.2. s2 – release of smoke from a construction product is significant, the index of smoke growth complies with the values specified in the testing standard;

19.3. s3 – the parameters obtained during testing are greater than the parameters specified in the classification standard for s2 intensity (practically the amount of smoke release is not limited);

19.4. d0 – a construction product does not release particles of burning droplets during burning;

19.5. d1 – presence of burning droplets is observed during burning of a construction product, but duration of burning thereof is not greater than that specified in the testing standard and they burn out rapidly; and

19.6. d2 – duration of burning of particles of burning droplets released by a construction product is greater than that specified for d1 intensity in the testing standard.

20. Reaction to fire classes of the floor covering shall be A1FL, A2FL, BFL, CFL, DFL, EFL and FFL. The intensity of smoke release from the floor covering shall be designated with the following symbols:

20.1. s1 – the total amount of smoke release is limited;

20.2. s2 – limitations for the amount of smoke release have not been specified.

21. Reaction to fire classes of the roof covering system as regards the influence of external fire shall be BROOF(t1), FROOF(t1), BROOF(t2), FROOF(t2), BROOF(t3), CROOF(t3), DROOF(t3), FROOF(t3), BROOF(t4), CROOF(t4), DROOF(t4), EROOF(t4) and FROOF(t4).

22. Reaction to fire classes of heat insulation products of pipelines shall be A1L, A2L, BL, CL, DL and EL.

23. The intensity of smoke release from heat insulation products of pipelines shall be designated with the symbols s1, s2 and s3.

24. The intensity of release of burning droplets from heat insulation products of pipelines shall be designated with the symbols d0, d1 and d2.

2.5. Fire Load

25. There are following groups of fire load of premises:

25.1. with fire load over 1200 MJ/m2;

25.2. with fire load from 600 MJ/m2 to 1200 MJ/m2 (including);

25.3. with fire load from 300 MJ/m2 to 600 MJ/m2 (including); and

25.4. with fire load which is less than 300 MJ/m2.

26. Fire load of a room g (expressed in MJ/m2) may be specified, using the following formula:

g=QS, where

S – area of the room (m2);

Q – total amount of burning heat of the room (MJ). It shall be calculated, using the following formula:

, where

Gi – amount of i-material (kg);

Qi p – amount of burning heat of a unit of i-material (MJ/kg).

27. If there are fire compartments in a structure, the fire load of which differ, the fire load of each fire compartment shall be calculated separately. Structures and elements thereof shall be classified in compliance with the fire load of the fire compartment with greater fire load.

28. A structure, which has different purposes of use, may be divided in separate groups of fire load. The requirements for fire resistance of bearing structures and fire compartments of a structure shall be determined in compliance with the relevant group of fire load.

3. Provisions for Planning of Structures

3.1. Fire Safety Intervals

29. In order to limit the possible flame spread in case of fire from one structure referred to in Paragraph 5 of this Construction Standard to another, fire safety intervals shall be observed between the structures. The minimum fire safety intervals between structures are specified in Table 7 of Annex to this Construction Standard, moreover, the minimum fire safety distance up to the boundaries of adjacent land units for the structures with fire stability level U1 and U2 shall be four metres, for U3 structures – five metres. Fire safety intervals between structures shall also be observed, if the structures are located in one land unit.

30. Fire safety intervals between structures in one land parcel need be not observed, if the construction area of structures is not greater than the maximum permissible values of a fire compartment specified in Table 3 of Annex to this Construction Standard. If fire stability levels of structures are different, fire safety interval shall be taken according to the structure with the lowest fire stability level.

31. The determined fire safety intervals and the minimum fire safety distance up to the boundary of adjacent land units may be reduced, if fire-proof wall has been arranged between the structures in compliance with the requirements specified in Table 1 of Annex to this Construction Standard.

32. A structure may be located closer than the minimum distance up to the boundary of an adjacent land parcel referred to in Paragraph 29 of this Construction Standard, not providing for a fire-proof wall if:

32.1. the structure is located next to land parcels, for which the status of a street, road or square has been determined in the territorial planning of a local government; or

32.2. the planned distance between adjacent structures in different land parcels complies with the distance specified in Table 7 of Annex to this Construction Standard.

33. The minimum fire safety intervals between few-storey residential houses located on two adjacent land parcels may be reduced, if the total area of the storeys of structures is not greater than the maximum permissible values of a fire compartment specified in Table 3 of Annex to this Construction Standard. If fire stability levels of structures are different, the fire safety interval shall be determined according to the structure with the lowest fire stability level.

34. In case of reconstruction and renovation it is allowed to retain the existing spaces between structures, if dimensions of structures are not increased in the direction of the fire safety interval.

3.2. Provision of Firefighting and Rescue

35. At least two drives suitable for firefighting and rescue equipment shall be ensured for structures of different types of use or groups thereof, which are located in an enclosed territory, the area of which is larger than five hectares.

36. If a perimeter of the enclosed territory, in which structures are located, is longer than 1000 metres, at least one drive is necessary for firefighting and rescue equipment per each 500 metres of the perimeter and they shall be placed regularly along the entire perimeter. If the enclosed edge along roads or streets is longer than 500 metres, at least two drives are necessary for firefighting and rescue equipment on the relevant edge. The distance between drives in the part of the perimeter along streets and roads may not exceed 500 metres, but in the remaining part of the perimeter – 1000 metres.

37. The width of access roads, drives and thoroughfares intended for firefighting equipment shall be at least 3.5 metres, height – at least 4.25 metres. It is allowed to retain the existing dimensions for structures to be reconstructed, renovated and restored.

38. The gates of drives and thoroughfares shall be equipped with devices which allow manual opening thereof.

39. Firefighting access road shall be ensured at least from one side of facade for structures, the mark of floor level of the highest storey of the which exceeds eight metres. If the structure is wider than:

39.1. 36 metres, firefighting access roads are necessary to both longitudinal facades at least in the length of 50% of each facade side;

39.2. 100 metres, firefighting access roads are necessary along the entire perimeter of a structure at least in the length of 50% of each facade side.

40. Access of firefighting and rescue equipment to a structure shall be ensured by 3.5 m wide access road which is located in the distance of five to 20 metres from the facade of the structure.

41. Parking lots and other obstacles may not be arranged on the access roads intended for firefighting and rescue equipment. Sufficient durability complying with the load of firefighting and rescue equipment shall be ensured for access roads. They shall be designated in compliance with the standard LVS 446:2004/A1:2006 “Safety signs and signal colouring used for fire safety and civil protection”. Lawn may be arranged on access roads with appropriately fixed base structure.

42. In case of renovation and reconstruction of structures the requirements referred to in Paragraphs 40 and 41 of this Construction Standard may be derogated, if the existing situation is not deteriorated for access of firefighting and rescue equipment.

43. Hydrants intended for the firefighting needs must comply with the requirements of standards LVS EN 14339:2007 “Underground fire hydrants”, LVS EN 14384:2007 “Pillar fire hydrants” and LVS 187:2007 “National requirements for fire hydrants”.

3.3. Openable Openings

44. Openable openings shall be built so as to be easily opened from inside of a structure. Sum of the free height and width of an openable opening shall be at least 1.5 m and minimum length of the edge – 60 cm.

45. The distance from the lower edge of an openable opening to the floor level may not exceed 1.2 metres.

3.4. Fire-resistant Building Structures

46. Fire-resistant building structures shall retain loadbearing capacity for a specified period of time in case of fire so that the people present in the structure could leave the structure immediately or they could be evacuated or rescued otherwise. Building structures shall not cause unforeseeable threat to the operation of firefighting and rescue services.

47. A building structure which is intended for the prevention of flame spread or delimiting of flame and smoke shall be regarded as a fire-resistant building structure. The minimum fire resistance of fire-resistant building structures is specified in Table 1 of Annex to this Construction Standard and the minimum reaction to fire class of construction products is specified in Table 2 of Annex to this Construction Standard.

48. Construction products built in fire-resistant building structures shall not reduce the fire resistance of a fire-safe structure and the fire resistance of mounting components placed therein shall not be lower than the fire resistance of the building structure itself.

49. Fire resistance of building structures shall comply with the requirements specified in Table 1 of Annex to this Construction Standard. Boundary structures of a room, separated by a fire-resistant structures shall be allowed such as to comply with the requirements of integrity and heat radiation permeability (EW), if fire load does not exceed 300 MJ/m2 in the premises, and in addition they shall be equipped with water curtains (sprinklers), if the fire load exceeds 300 MJ/m2 in such premises.

3.5. Protection of Openings and Engineering Systems in Fire-safe Structures

50. It is allowed to arrange in a fire-safe structure openings with non-openable and openable filling, the total area of which does not exceed 25% of the area of the fire-safe structure. Fire resistance of openable filling of openings (doors, gates, windows, manholes, blinds, fire-proof curtains and fire dampers) may be by 50% lower than the fire resistance determined for fire-safe structures, but not lower than EI 30.

51. The minimum fire resistance of fillings of openings (windows, doors or manholes) present in fire walls and fire-safe structures and the minimum reaction to fire class is specified in Tables 1 and 2 of Annex to this Construction Standard.

52. If openings located in different fire compartments are at angle one against another, then:

52.1. if angle is less than 60°, fire resistance of filling of openings shall comply with the requirements specified in Table 1 of Annex to this Construction Standard;

52.2. if angle is within the borders from 60° to 135°, the filling of openings shall comply with the requirements of integrity (E) and heat radiation limitation (W) which are specified in Table 1 of Annex to this Construction Standard; or

52.3. if angle is larger than 135°, additional requirements shall not be specified for the fire resistance of the filling of openings.

53. Engineering communications crossing fire-safe structures shall be built so as not to reduce the fire resistance of fire-safe structures and not to allow the spread of smoke, gas and flame.

54. Gaps at the places of crossing of fire-resistant building structures and engineering communications shall be filled up with such construction products in the entire thickness of structures, reaction to fire class of which is not lower than the minimum reaction to fire class of the fire-resistant building structures. Compacting of the unit of crossing of fire-resistant building structures and engineering communications is permissible with fire-proof sealing or systems, reaction to fire class of construction products of which is at least Bs1,d0, which upon reaction to fire ensures air tightness of communications, closing of insulation of burning pipes and cables and the conformity of which is confirmed in accordance with the procedures specified in the Law On Conformity Assessment.

55. Openable fillings of openings built in fire-safe structures shall be equipped with self-closing mechanisms, which shall close the openings in case of fire in order not to allow the spread of fire and burning products.

4. Requirements for Building Structures

4.1. Fire Compartments and Room Separated by Fire-resistant Structures

56. Fire compartments and a room, separated by a fire-resistant structures shall be delimited from other compartments and premises with fire-resistant building structures. The minimum fire resistance and the minimum reaction to fire class of fire-resistant building structures is specified in Tables 1 and 2 of Annex to this Construction Standard.

57. The permissible area of a fire compartment and the area of storeys within the framework of a fire compartment shall depend on the height, type of use and fire stability level of the structure. The maximum area of a storey or fire compartment is indicated in Table 3 of Annex to this Construction Standard.

58. Fire compartment may include one or several storeys of a structure. Each storey of a fire compartment shall be separated with fire-resistant building structures, the fire resistance and minimum reaction to fire class of construction products of which has been standardised and is specified in Tables 1 and 2 of Annex to this Construction Standard. If storeys are not separated with fire-resistant building structures, the total area of such storeys shall not exceed the maximum area of fire compartment, which is specified in Table 3 of Annex to this Construction Standard.

59. Structures shall be divided in separate fire compartments, the area of which does not exceed permissible area of fire compartment, which is specified in Table 3 of Annex to this Construction Standard.

60. Structures with different type of use shall be designed as separate fire compartments. This requirement shall not apply to built-in premises.

61. In a structure of one type of use the groups of premises of other type of use shall be intended as a room, separated by a fire-resistant structures. It is allowed not to intend the following as a room, separated by a fire-resistant structures, i.e., not to separate in a fire-safe manner:

61.1. in structures of type of use VI – the groups of premises of type of use V;

61.2. in structures of type of use II, III, IV, IVa and V – premises of type of use II, III, IV, IVa and V.

62. The following shall be formed as separate a room, separated by a fire-resistant structures:

62.1. storeys of a structure within the framework of fire compartment;

62.2. apartments and hotel rooms;

62.3. premises of technical devices, the area of which is larger than 10 m2 or the fire load is larger than 600 MJ/m2;

62.4. elevator shafts, except elevator shafts located in staircases, atria and outside structures;

62.5. engine rooms of elevators and elevator lobbys;

62.6. fire protected and smoke-protected stairways;

62.7. protected escape routes;

62.8. groups of premises of a bathhouse;

62.9. shafts of engineering communications with non-compacted openings on the level of inter-storey coverings;

62.10. premises for pumps of fixed firefighting systems and control units thereof; and

62.11. fire safety lobbys.

63. In structures of fire stability level U3 the fire resistance and reaction to fire class of building structures of a room, separated by a fire-resistant structures shall not be standardised, except the cases specified in other regulatory enactments.

4.2. Fire Walls

64. The minimum fire resistance limit values of fire walls are specified in Table 1 of Annex to this Construction Standard.

65. In fire walls it is allowed to build in the construction products, the reaction to fire class of which is not lower than the class specified in Table 2 of Annex to this Construction Standard.

66. Fire walls shall be designed in the entire height and width of a structure and they shall cross all structures of the structure. Stability and loadbearing capacity shall be ensured for the wall so that a failure of the structures in one side of the wall would not deteriorate the strength, stability and other properties of the fire-proof wall. Communication and structural elements mounted in the fire-proof wall or located on it or closely next to it shall not cause additional load or deformations reducing the strength or stability of the fire-proof wall.

67. Connection points of fire walls with other structural elements, as well as crossings of communications through a fire-proof wall shall be formed of appropriate materials of reaction to fire so as not to deteriorate the functions of the fire-proof wall.

68. A fire-proof wall need not cross structures of the roof and external walls, if reaction to fire class of construction products built in the structures of roof and external walls is at least A2-s1,d0.

69. It is not allowed to install crossings of ventilation air ducts and channels in fire walls, as well as to install crossings of such communications, along which combustible materials are conveyed.

70. If reaction to fire class of construction products built in building structures of the roof and external walls is lower than A2-s1,d0, fire walls shall be at least by 60 cm higher than the surface of the roof covering and protruded by at least 30 cm out of the plane of the external wall. This requirement is not mandatory, if at the connection point of a fire-proof wall with structural elements of the roof and external wall a fire separation element with width of two metres is intended in the roof and external wall (one meter to each side from the fire-proof wall), performing the functions of a fire-proof wall.

71. If the difference in height of roofs of different levels at the fire-proof wall is larger than 30 cm, the fire-proof wall shall be by at least 30 cm higher than the level of the highest roof.

4.3. External Walls

72. The minimum fire resistance of the structures of external walls and the minimum reaction to fire classes of construction products to be used are specified in Tables 1, 2 and 5 of Annex to this Construction Standard. Fire resistance and reaction to fire of fillings of openings of external walls (except fillings of openings installed in fire walls) shall not be standardised.

73. In each storey of a structure, if it forms a fire compartment, a horizontal fire separation element with width of 0.8 metres, the fire resistance of which is not lower than fire resistance of covering, shall be installed in the external wall on the level of inter-storey covering. The fire resistance of external walls shall not be standardised and horizontal fire separation elements are not necessary, if the structure is equipped with automatic firefighting system or if water curtain of automatic firefighting system protection is arranged along the internal perimeter of the structure (if the total area of storeys does not exceed the permissible area of fire compartment, which is specified in Table 3 of Annex to this Construction Standard).

74. Reaction to fire class of a joint (membrane) of an external wall and covering shall not be lower than the reaction to fire class of the covering.

75. In a structure, the floor level of the highest storey of which exceeds 28 metres, an automatic firefighting system shall be intended with double external walls or an automatic firefighting water curtain shall be intended for the protection of openings of external walls from the inside on each storey of the structure. A double external wall is an external wall without openable openings, the external delimiting structure of which is delimited from supporting wall structure with a gap exceeding 10 cm.

76. Coverings shall fit tight to external walls without spaces.

4.4. Attics and Cocklofts

77. Attics shall be separated from other premises with structures, the minimum fire resistance and reaction to fire class of building products of which is specified in Tables 1 and 2 of Annex to this Construction Standard.

78. In structures, the height of which from the road (ground) level up to a cornice or upper edge of a parapet is larger than 10 metres, an exit from the attic to the roof through doors, manholes or windows, the minimum free size of which is 0.6 x 0.8 metres, shall be arranged in each fire compartment. If the height up to a lower edge of the exit is larger than 1.5 metres, fixed stairs shall be arranged.

79. In structures, the height of which from the road (ground) level up to a cornice or upper edge of a parapet is larger than 10 metres, an exit shall be built from each staircase, which leads up to the last (upper) storey, to the attic through fire-proof door or manhole with minimum size of 0.6 x 0.8 metres and fixed stationary vertical or draw-out stairs made of construction products of reaction to fire class A1.

4.5. Roofs

80. The requirements for bearing structures of roofs are specified in Tables 1 and 2 of Annex to this Construction Standard.

81. In structures, the height of which from the road (ground) level up to a cornice or upper edge of a parapet is larger than 10 metres:

81.1. an exit shall be intended from each staircase, which leads up to the last (upper) storey:

81.1.1. directly to the roof along fixed stationary or draw-out stairs through a fire-proof manhole, the minimum size of which is 0.6 x 0.8 metres;

81.1.2. to the roof along stairs through fire doors, the minimum size of which is 0.75 x 1.5 metres, and the attic in accordance with Paragraph 78 of this Construction Standard;

81.1.3. to the roof through the attic in accordance with Paragraph 79 of this Construction Standard;

81.2. a roof enclosing shall be built along the perimeter of the structure in the height of at least 300 mm or horizontal bars (wire ropes) shall be arranged in the cornice of the roof for fixing of safety devices. A roof enclosing for flat roofs shall be arranged in the height of at least 600 mm. If the slope of the roof is more than 40°, an enclosing shall not be arranged, but stairs shall be arranged from exit manholes up to the cornice of the roof or horizontal bars (wire ropes) shall be arranged in the cornice of the roof for fixing of safety devices.

82. In a structure, the floor level of the highest storey of which exceeds 28 metres and reaction to fire class of construction products used in a roof covering system is lower than A2-s1,d0, a roof covering, the reaction to fire class of which to exposure of external fire is not lower than BROOF(t1), shall be intended.

83. If the roof of the structure is on different levels and the difference of heights is larger than one metre, the relevant parts of the roof shall be connected with external firefighting stairs manufactured from material of the reaction to fire class A1.

4.6. Balconies, Loggias, Terraces, Passages and Galleries

84. The minimum fire resistance of the building structures of balconies, terraces, passages and galleries and the minimum reaction to fire classes of construction products to be used are specified in Tables 1, 2 and 5 of Annex to this Construction Standard.

85. The fire resistance requirements to be set for structures of bays shall be identical to the fire resistance requirements specified for bearing structures of the structure.

4.7. Atria

86. Atria within the meaning of this Construction Standard shall be a covered internal room of the building, which consecutively connects three and more storeys. Staircases, elevator shafts and shafts of engineering communications are not atria.

87. An atrium shall be made in one of the following ways:

87.1. as a a room, separated by a fire-resistant structure;

87.2. together with premises adjacent to atria as a fire compartment the area of which – the sum of areas of all premises therein – shall not exceed the maximum area of fire compartment specified in Table 3 of Annex to this Construction Standard.

88. If an atrium is made in compliance with Sub-paragraph 87.2 of this Construction Standard:

88.1. the atrium shall be delimited from the premises adjacent thereto by forming a smoke barrier and an automatic firefighting curtain; and

88.2. an automatic firefighting system shall be arranged in the premises present in the fire compartment adjacent to the atrium.

89. The fire load exceeding 300 MJ/m2 shall not be permissible in the main composition of the atrium. The fire load shall not be standardised in the premises adjacent to the atrium.

90. The doors located in the boundary structures of the atria shall be equipped with self-closing mechanisms.

4.8. Explosion Protection Measures

91. Protection of structures or premises against explosions shall be determined, taking into account the possible concentration of combustible substances, gases, steam, drops or dust mixture in the air (hereinafter – explosive environment) in compliance with the regulatory enactments regulating fire safety.

92. The explosive room shall be determined, taking into account the amount of substances and materials necessary for the technology and the fire hazard and explosion hazard indicators of substances and materials.

93. Explosion protection measures shall be intended in order:

93.1. to prevent formation or ignition of explosive environment; and

93.2. to reduce the influence caused by explosion.

94. In order to limit the spread of an explosive environment:

94.1. the explosive room shall be formed as a a room, separated by a fire-resistant structure;

94.2. exits and entrances of explosive rooms to other premises shall be arranged through a fire-proof lobby and measures limiting the spread of the explosive environment in a structure shall be intended;

94.3. sealing of communication entries shall be performed.

95. Explosive premises shall be located by the external delimiting structure of the structure.

96. The requirements of this Sub-chapter shall not apply to structures, in which operations with explosives, for which oxygen is not necessary, take place.

5. Escape Routes and Exits

97. Escape routes and emergency exits shall be arranged for evacuation of people from structures and premises in case of fire and other danger or threats.

98. The following requirements shall be set for an escape route:

98.1. it shall be easy to find;

98.2. the finishing of walls and ceiling and the covering of floor shall not endanger the safety of users during evacuation;

98.3. it shall not be obstructed by objects and devices which endanger the safety of users during evacuation; and

98.4. in structures of type of use III it shall be made as a corridor, which complies with the environment accessibility requirements.

99. If the difference between floor levels in escape routes exceeds 20 mm, but for doorsteps of fire doors – 25 mm, a slope (ramp), the obliquity of which is not larger than 1:12, or at least three steps, the geometry of which complies with the requirements of the construction standards regulating designing of the relevant structure, shall be built at the places of change in the floor level. If the difference between floor levels of premises in a vertical projection is more than 0.45 m, the stairs or ramp shall be fitted with handrails.

100. In structures of all fire stability levels (except structures of the fire stability level U3):

100.1. the reaction to fire class of construction products of the finishing of walls and ceilings in fire protected staircases and protected escape routes shall be at least A2-s1,d0 and the reaction to fire class of construction products of floors shall be at least BFL;

100.2. in vestibules, atria, halls and lobbys the reaction to fire class of construction products of walls and ceilings shall be at least Bs1,d0 and the reaction to fire class of construction products of floors shall be at least DFL.

5.1. Emergency exits

101. Emergency exits shall be openable easily and without any effort from the interior, including for persons with special needs. Emergency exits shall ensure safe exit of persons to be evacuated from a structure and premises thereof directly outside on the level of ground surface or:

101.1. along staircase;

101.2. along open stairs;

101.3. along a protected escape route;

101.4. along a protected escape route and staircase;

101.5. along a protected escape route and open stairs; or

101.6. through another fire compartment.

102. The number and layout of emergency exits shall be determined in compliance with the type of use of a structure, the intended maximum number of users of the structure and the distance up to the emergency exit in compliance with Table 6 of Annex to this Construction Standard.

103. The summary width of emergency exits in multi-storey structures shall not be less than the summary width of escape routes determined in Paragraphs 143 and 144 of this Construction Standard, taking the maximum number of users in the storey with the largest area or the largest number of users as the basis for the calculation.

104. The possibility to evacuate at least through two separate places shall be ensured from a structure, fire compartments thereof, storeys of a structure and premises of a structure where users of the structure stay permanently, except the cases referred to in Paragraph 112 of this Construction Standard.

105. At least three emergency exits shall be built from premises or storeys, in which more than 500 users are staying, and at least four emergency exits – from premises or storeys, in which more than 1000 users are staying.

106. The minimum distance between the nearest emergency exits in premises shall be determined, using the following formula:

, where

P – perimeter (m) of the room or fire compartment; and

n – number of emergency exits.

107. In structures, the mark of floor level of the highest storey of which does not exceed 28 metres, one of emergency exits from the storeys of the structure may be intended along the external open oblique or winding stairs. Other emergency exits shall comply with the requirements referred to in Sub-paragraph 101.1, 101.3 or 101.4 of this Construction Standard.

108. One of emergency exits from storeys of a structure may be intended through another fire compartment. Other emergency exits shall comply with the requirements referred to in Sub-paragraph 101.1, 101.3 or 101.4 of this Construction Standard. It is allowed to intend evacuation only through one fire compartment.

109. It is not allowed to use elevators and devices analogue thereto for evacuation.

110. It is not allowed to intend evacuation through technical a room, separated by a fire-resistant structures and premises with explosive environment.

111. It is not allowed to intend evacuation in the structures of type of use I, II, III, IV, IVa and V through the structures and premises of type of use VI and VII.

112. One emergency exit from a storey is permissible in the following structures:

112.1. in structures of the type of use I where the floor level of the highest storey does not exceed eight metres;

112.2. in structures of the type of use I where the floor level of the highest storey does not exceed 28 metres, if evacuation is intended only from apartments through a fire protected staircase and there is openable opening in each apartment;

112.3. in structures of the type of use I where the floor level of the highest storey does not exceed 75 metres, if evacuation is intended through smoke-protected stairway of type 1, the total area of apartments in one storey is more than 500 m2 and premises of other types of use, which are not related to the provision of exploitation of the building, have not been built in the storeys;

112.4. in structures of the types of use V, VI and VII where the floor level of the highest storey does not exceed 28 metres, the length of escape route does not exceed 30 metres, it is intended that not more than 50 users will stay in the storey and there is an openable opening in each group of premises or storey;

112.5. in structures of the types of use II, III and IVa where it is intended that not more than 50 users will stay and there is an openable opening in each storey;

112.6. in structures where the floor level of the highest storey does not exceed 28 metres, if evacuation is intended through a smoke-protected stairway and the length of escape route does not exceed 30 metres; and

112.7. in open structures.

5.2. Stairs and Staircases

113. Fire protected and smoke-protected stairways, as well as open stairs and external escape stairway shall be intended for evacuation of users of a structure and operation of the firefighting and rescue service.

114. The minimum fire resistance and the minimum reaction to fire class of building structures of staircases is specified in Tables 1 and 2 of Annex to this Construction Standard.

115. External escape stairway shall be built with oblique flights or in winding way from construction products of the reaction to fire class A1.

116. In structures where the mark of floor level of the highest storey does not exceed 28 metres, smoke-protected stairways shall be constructed. In structures where the mark of floor level of the highest storey does not exceed 50 metres, emergency power supply for the automatic fire protection systems and devices shall be intended from a generator with internal combustion engine. A generator with internal combustion engine need not be intended in structures where at least one of staircases is a smoke-protected stairway of type 1.

117. Depending on technical solutions by which the possibility of smoke formation is prevented, the following smoke-protected stairways shall be distinguished:

117.1. type 1 – connection of a staircase with other premises is arranged on the level of storeys through an open external zone (balconies, loggias, open passages and galleries) and a direct exit to the outside on the level of ground surface;

117.2. type 2 – air overpressure is ensured in a staircase in case of fire in the entire volume thereof; and

117.3. type 3 – connection of a staircase with other premises is arranged through a fire-proof lobby where air overpressure is ensured in case of fire.

118. Exits from smoke-protected stairways on the level of ground surface shall be arranged directly to the outside or through a fire-proof lobby where the possibility of smoke formation is prevented. In such case the fire resistance of building structures and the reaction to fire class of construction products of a fire-proof lobby shall be not lower than the fire resistance of building structures and the reaction to fire class of construction products.

119. Fire protected and smoke-protected stairways (except smoke-protected stairways of type 1) may be connected with a plinth storey or basements through a fire-proof lobby.

120. The free width of flights of stairs and landings shall not be less than the minimum width of escape route, as well as than the width of exits (doors) and openings intended for evacuation. The free width of flights of stairs shall not be less than:

120.1. 1400 mm – for a fire compartment, from which evacuation of more than 250 users is intended;

120.2. 1200 mm – for a fire compartment from which evacuation of more than five users is intended;

120.3. 700 mm – for stairs along which evacuation of not more than five users is intended.

121. It is allowed to retain the existing dimensions of staircases in structures to be renovated and reconstructed.

122. Exits from fire protected staircases on the level of ground surface shall be arranged directly to the outside or through a a room, separated by a fire-resistant structure, the fire resistance of building structures and the reaction to fire class of construction products of which complies with the fire resistance of building structures and the reaction to fire class of construction products of staircases.

123. It is allowed to round the corners of the landing of stairs and change the geometry thereof, if the width of an escape route specified in this Sub-chapter is retained along the radius.

124. The slope of stairs in escape routes shall not be more than 1:1, the width of a step shall be at least 250 mm, a step shall not be higher than 220 mm.

125. It is allowed to build the stairs, which are intended for not more than five users, with a slope of 2:1.

126. The narrowest edge of a step of curvilinear or winding stairs shall be at least 220 mm, but for stairs that are intended as the second emergency exit from premises which are intended for up to 25 users – up to 120 mm. The width of stairs shall be determined in compliance with Paragraph 120 of this Construction Standard.

127. It is not allowed to arrange such premises in staircases which are intended for other purpose of use, to place pipelines which are intended for liquefied gas or combustible solutions, ventilation ducts, built-in closets, openly placed power supply cables or wires for voltage above 230V, exits from cargo elevators or hoists, as well as locate devices and building structures which are protruded outside the planes of walls up to the height of 2.2 metres from steps or landings of stairs.

128. The distance between flights of stairs shall be at least 50 mm or other measures shall be intended which ensure the water supply necessary for firefighting in the upper storeys of a structure.

129. It is allowed to build in and place openly the cabinets for communications and devices of fire hoses and heaters in staircases, if they do not reduce the width of escape route and fire resistance of walls of staircases.

130. In structures where the mark of floor level of the highest storey does not exceed 28 metres it is allowed to arrange waste ducts in staircases, if the reaction to fire class thereof is not lower than A2-s1,d0 and if it is not in contradiction with the local government local construction regulations. If the reaction to fire class of construction products of waste duct is lower than A2-s1,d0, it shall be placed in a a room, separated by a fire-resistant structure.

131. In structures of type of use III and in educational institutions emergency stairs shall not be winding, if the diameter of the middle aperture is less than 1000 mm. The narrowest edge of the step of stairs shall not be narrower than 220 mm. The width of stairs shall be determined in compliance with the width of the necessary escape route.

132. The stairs on escape routes shall be equipped with handrail.

133. An openable opening shall be intended in an external delimiting structure on the level of each storey for smoke exhaust in a fire protected staircase.

134. In structures where the mark of floor level of the highest storey does not exceed eight metres, and there are no openable smoke exhaust openings in external walls of the fire protected staircase on each storey, a smoke exhaust opening shall be intended in the upper zone of the staircase where the area of free opening is at least 5% of the area of staircase and is not less than 1 m2.

135. If there is no smoke exhaust openings in a fire protected staircase in compliance with the requirements referred to in Paragraphs 133 and 134 of this Construction Standard, a smoke-protected stairway shall be intended.

136. It is not allowed to arrange openings in internal walls of a staircase (except door openings).

137. The width of external door of a staircase may not be lesser than the minimum width of emergency exits specified in Paragraph 120 of this Construction Standard.

138. The distance from the door of the staircase up to the windows in smoke-protected stairways of type 1 with exit from a storey through external separated zone shall be not lesser than two metres.

139. It is not allowed to intend elevator exits in smoke-protected stairways of type 1.

140. The fire resistance of fillings of openings (which are directed against external escape stairway that are intended as an emergency exit from storeys of a structure, as well as for the fire resistance of external boundary structures) shall be at least EI-30 in the distance of two metres from the stairs.

5.3. Length of an Escape Route

141. The length of an escape route and the area of room to be calculated for one user shall be determined in compliance with Table 6 of Annex to this Construction Standard. The length of an escape route from a dead end zone shall be determined as 50% of the distance specified in Table 6 of Annex to this Construction Standard. If the length of an escape route exceeds the distance specified in Table 6 of Annex to this Construction Standard, a protected escape route shall be created.

142. The length of an escape route from premises, the area of which is not more than 50 m2, up to the emergency exit shall be determined from the exit door of a room, if it opens in the evacuation direction.

5.4. Dimensions of an Escape Route

143. The minimum width of an escape route shall be at least 1.20 metres, but in medical treatment and care institutions – at least 1.80 metres. It is allowed to reduce the width of an escape route up to one metre, if it is intended for evacuation of up to 50 persons.

144. If the number of persons to be evacuated from a room or from premises located in one storey exceeds 250 users, the summary width of an escape route for each next 100 users shall be increased by 50 cm.

145. When calculating the width of an escape route, the width of door leaves shall be taken into account, which open from premises in the direction of the escape route and may disturb the use of the escape route, reducing the standard width of the escape route. In such case the width of the corridor calculation in the calculation of the width of the escape route shall be reduced by:

145.1. a half of the width of the door leaf, if the doors are located in one side of the corridor;

145.2. the width of the door leaf, if the doors are located in both sides of the corridor in the stage which is shorter than doubled width of the corridor.

146. The free height of an escape route shall be at least two metres and in such height no obstacles shall be allowed. The height of an escape route in basements, where not more than five users are intended to stay, shall be at least 1.90 metres.

5.5. Doors

147. In emergency exits the doors shall:

147.1. open in the direction of evacuation, except the doors in structures, parts or premises thereof where the number of users is lesser than 25, or the doors which lead to another fire compartment;

147.2. not disturb users with movement disorders to use the relevant means of movement;

147.3. be openable without a key or other auxiliary means in case of fire (also without electronic key), except the doors which separate staircases from apartments; and

147.4. be equipped with self-closing mechanism, except the doors of apartments.

148. Fire-proof two-leaved doors shall be equipped with self-closing mechanisms which consecutively close the door leaves.

149. The free height of the doors in escape routes and exits shall be at least two metres. It is allowed to reduce the height of the doors and passages, which lead to the outside from a technical storey where not more than five users are intended to stay, up to 1.9 metres, but the doors to exits to the attic or roof – up to 1.5 metres. The free height of the doors shall be at least 0.9 metres.

150. The requirements referred to in Paragraph 147 of this Construction Standard shall not apply to the structures of type of use III with specific internal mode, as well as to the structures where such persons are accommodated for whom the competent authorities have limited freedom of movement. In such premises other measures shall be intended, which ensure evacuation of persons in case of fire.

151. If evacuation is intended from one fire compartment to another, the direction of door opening shall be from that fire compartment where a greater number of users may stay.

152. The minimum fire resistance of the doors of a staircase and the minimum reaction to fire class of building structures is specified in Tables 1 and 2 of Annex to this Construction Standard. In structures where the mark of floor level of the highest storey does not exceed 28 metres, the fire resistance of the door of a staircase shall be at least EI-60.

153. If the doors built in the fire-safe structures of the structure should be in an opened position in compliance with the type of use or technology requirements, automatic devices shall be intended, which ensure closing of the doors in case of fire after receipt of a signal from automatic fire protection systems.

154. Sliding, lift-off (turn-down) and rotating door (except external door, if the possibility of manual opening is ensured for it in case of evacuation) shall not be built in escape routes. When constructing a rotating door, the construction of an openable door shall be intended additionally, ensuring the minimum dimensions of emergency exits.

155. The fire-proof door which is constructed in fire-resistant building structures (except the doors of technical premises and the doors of apartments) shall be equipped with a self-closing mechanism.

156. The fire resistance of external doors and the reaction to fire class of construction products shall not be standardised (except the doors which are located in fire walls and the doors which lead to external escape stairway).

5.6. Fire Elevators

157. In structures where the mark of floor level of the highest storey exceeds 50 metres, at least one fire elevator shall be intended. The requirement shall not apply to structures or parts of the structure where permanent users are not staying.

158. Fire elevators shall be designed and constructed, observing the following conditions:

158.1. fire elevator shafts shall be separated from other premises in a fire-safe manner, including from elevator shafts of other significance;

158.2. the size of the fire elevator cabin shall be at least 1.1 x 1.4 metres;

158.3. each stop of the fire elevator shall be equipped with a fire-proof lobby.

159. The main storey of boarding in fire elevators shall be the storey of the main entrance of the structure, which ensures direct fire-safe entry from outside or through a vestibule, the fire load of which is not larger than 300 MJ/m2.

5.7. Emergency Lighting and Designations of Evacuation

160. Emergency lighting of evacuation shall be the part of emergency lighting, which ensures lighting during evacuation of persons, if basic lighting is out of order.

161. Emergency lighting of evacuation shall be arranged:

161.1. in structures where the mark of floor level of the highest storey exceeds 28 metres, – in protected escape routes;

161.2. in escape routes, including in protected escape routes, if the number of persons to be evacuated is 50 and more;

161.3. in structures or premises of types of use II, III, IV, IVa and V, if there are more than 100 persons at the same time.

162. Emergency exits intended for evacuation of at least 50 persons shall be equipped with lighted-up emergency exit indicators.

163. Evacuation lighting networks and lighted-up emergency exit indicators shall be connected to two independent sources of power supply.

6. Smoke Protection of Structures

164. In order to limit the spread of smoke in case of fire or to ensure the smoke exhaust from premises, the following shall be intended in the structure:

164.1. automatic air overpressure systems;

164.2. smoke exhaust openings;

164.3. automatic smoke exhaust systems;

164.4. non-automatic smoke exhaust systems.

165. Automatic air overpressure systems shall be intended:

165.1. in smoke protected staircases of type 2;

165.2. in fire safety lobbys of smoke protected staircases of type 3;

165.3. in elevator shafts in the structures with smoke protected staircases;

165.4. in elevator lobbys, which are located in the structures with smoke protected staircases, if automatic overpressure smoke protection system of elevator shafts is not intended;

165.5. in protected escape routes where there are no smoke exhaust openings;

165.6. in the structures of types of use I, II, III, IV, IVa, V, VI and VII where the mark of floor level of the highest storey exceeds 28 metres and where there are smoke protected staircases in the protected escape routes.

166. The operation of an automatic air overpressure system shall be ensured in the storey, in which the fire has derived in the premises referred to in Sub-paragraphs 165.2, 165.4, 165.5 and 165.6 of this Construction Standard.

167. Smoke exhaust openings shall be intended in each storey of the fire compartment.

168. The distance from the fire compartment or any point in the storey up to the smoke exhaust opening shall not exceed 15 metres. The minimum area of the smoke exhaust opening shall be at least 0.5 m2.

169. The distance from any point up to the smoke exhaust openings in a separate room may be increased up to 30 metres, if the total area of the smoke exhaust openings is at least 0.2 % of the area of the room to be protected and they are located higher than two metres from the floor level of the room.

170. A non-automatic smoke exhaust system shall be intended:

170.1. in a fire compartment, storey and room where there are no smoke exhaust openings, which comply with the requirements referred to in Paragraph 168 or 169 of this Construction Standard;

170.2. in stages with the flies;

170.3. in the underground storeys, the floor of the lowest storey of which is located lower than four metres from the average level of the ground mark.

171. In the premises where it is not possible to arrange a non-automatic smoke exhaust system with natural exhaust, the smoke exhaust system with mechanical traction or mechanical compensation air supply shall be provided for.

172. An automatic smoke exhaust system shall be intended in atria.

173. Smoke exhaust need not be intended from:

173.1. the premises of structures of the type of use VI where the fire load does not exceed 600 MJ/m2;

173.2. other premises with area up to 50 m2 where the fire load does not exceed 300 MJ/m2;

173.3. the premises through which evacuation of persons does not take place, if the fire load does not exceed 300 MJ/m2 therein;

173.4. the structures of open type;

173.5. the structures of the fire stability level U3.

7. Automatic Fire Protection Systems and Devices

7.1. General Requirements

174. In compliance with the type of use of a structure or room and the layout of premises the following automatic fire protection systems and devices shall be intended:

174.1. autonomous fire detectors;

174.2. automatic fire detection and alarm systems;

174.3. automatic voice fire alerting system;

174.4. automatic firefighting systems, automatic cooling systems and automatic firefighting water curtains;

174.5. automatic air overpressure systems;

174.6. automatic smoke exhaust systems.

175. Automatic fire protection systems shall ensure, independently and in interaction with other engineering systems, the performance of the functions intended in regulatory enactments in the automatic and manual control mode.

176. An automatic fire protection system shall automatically transmit signals of alarm, damages, blocking devices and systems to the control and indicating device (panel), which is permanently monitored by the personnel. If the control and indicating device (panel), which is permanently monitored by the personnel, is not located with this system in one object to be protected, the alert shall also be transmitted to the light and sound alert device located in a visible place on the facade of the structure to be protected, which is placed at least 2.5 metres higher than the level of the ground surface (floor).

177. Automatic fire protection systems shall ensure:

177.1. uninterrupted day and night operation on duty (stand-by) mode;

177.2. uninterrupted power supply from at least two sources of electricity supply, and fire protection, which ensures the operation of the system for at least 30 minutes in case of fire, shall be intended for the installation of electric power supply;

177.3. on duty mode and operating modes – automatic control with acoustic and visual signalling of control (launching) circuits, electricity supply sources (basic and emergency) and capacity of communication lines.

178. The devices and installations intended for the installation and operation in explosive and chemically aggressive environment shall be used in automatic fire protection systems in the relevant environment.

179. The control and indicating device (panel) shall be placed in easily accessible places (premises), preferably – on the first storey or plinth storey of the structure.

180. The type of the automatic fire protection system shall be determined by the commissioning party in the designing order in compliance with regulatory enactments and technical regulations of manufacturers of the devices.

181. Voice, sound or visual signalling devices of the automatic fire protection system need be not intended in the structures and premises where the persons for whom competent authorities have limited freedom of movement are staying, as well as in the premises of medical treatment and care institutions where the persons not able to evacuate independently are staying. Fire alerting in such structures and premises shall be intended in accordance with the designing order.

7.2. Requirements for Autonomous Fire Detectors

182. Autonomous fire detectors shall be intended:

182.1. in the structures of type of use I. At least one autonomous fire detector which reacts to smoke shall be intended in each apartment;

182.2. in the structures of types of use II and III where there are no more than 10 places of accommodation. Detectors shall be placed in the premises intended for sleeping.

183. Autonomous detectors shall be installed in compliance with technical regulations of the manufacturer and designing order.

184. Autonomous fire detectors may be replaced by an autonomous fire detection and alarm system or by fire detectors which are connected to another system control and indicating device (panel).

7.3. Requirements for Automatic Fire Detection and Alarm Systems

185. Automatic fire detection and alarm systems shall be intended:

185.1. in the structures of types of use II and III where there are more than 10 places of accommodation;

185.2. in the structures and premises of types of use II, III, IV, IVa un V, the total area of which is more than 200 m2;

185.3. in the structures and premises of type of use VI (except reservoirs), the total area of which exceeds 50 m2 and where pumping, pouring, release, prepacking or storage of oil, oil products and other inflammable substances is intended;

185.4. in the structures and premises of types of use VI and VII, the total area of which is more than 1000 m2 and the fire load of which is more than 300 MJ/m2;

185.5. for control of other automatic fire protection systems for which, in compliance with regulatory enactments and designing order, automatic control mode is necessary.

186. An automatic fire detection and alarm system need not be intended in the structures of open type and auxiliary buildings of few-storey residential houses.

187. An automatic fire detection and alarm system shall be designed, ensuring automatic detection of fire and transmission of alarm signals in each room in the structures referred to in Paragraph 185 of this Construction Standard, except:

187.1. sanitary and technical premises, the fire load of which is less than 25 MJ/m2;

187.2. shafts of engineering communications; and

187.3. refrigerators, the capacity of which is less than 20 m3.

188. In the structures where arrangement of an automatic fire detection and alarm system is intended, fire detectors which react to smoke shall be installed in the protected escape routes and staircases.

189. In case of fire detection the automatic fire detection and alarm system shall send a signal to the control of other firefighting engineering systems in compliance with regulatory enactments and designing order.

190. An automatic fire detection and alarm system need not be intended in the premises where the functions thereof are performed by another automatic fire protection system, observing the requirements referred to in Paragraph 188 of this Construction Standard.

7.4. Requirements for Automatic Voice Fire Alerting Systems

191. Automatic voice fire alerting systems shall be intended:

191.1. in the structures of types of use II, IV, IVa and V where the mark of floor level of the highest storey exceeds 28 metres or where more than 500 users may stay at the same time;

191.2. in the structures of type of use III where the mark of floor level of the highest storey exceeds eight metres and where there are at least 50 places of accommodation; and

191.3. in the buildings and premises of museums and exhibitions the total area of which exceeds 1000 m2.

192. An automatic voice fire alerting system shall be designed in the structures referred to in Paragraph 191 of this Construction Standard, ensuring the comprehensibility of alarm voice announcement in each room where persons may be present.

193. In the structures where the mark of floor level of the highest storey does not exceed 28 metres, alerting zones may be intended in the automatic voice fire alerting system which alert the information in several storeys at the same time. In the structures where the mark of floor level of the highest storey exceeds 28 metres, one alerting zone shall not be larger than one storey of the structure.

194. In the structures where the mark of floor level of the highest storey exceeds 28 metres, the automatic voice fire alerting system shall be designed so as fire can be alerted in the automatic and manual control mode in the storeys in the following order:

194.1. in alerting zones in the storey where the fire has derived;

194.2. in alerting zones above the storey where the fire has derived; and

194.3. in other alerting zones.

7.5. Requirements for Automatic Firefighting Systems, Automatic Water Cooling Systems and Automatic Firefighting Water Curtains

195. Automatic firefighting systems shall be intended:

195.1. in fire compartments the area of which exceeds the maximum permissible area specified in Table 3 of Annex to this Construction Standard;

195.2. in the structures of type of use I where the mark of floor level of the highest storey exceeds 75 metres;

195.3. in the structures (except the structures of type of use I) where the mark of floor level of the highest storey exceeds 50 metres;

195.4. in the underground storeys of the structure, the area of which is more than 1000 m2 and where the floor of the lowest storey is located lower than four metres from the average level of the ground mark;

195.5. in the structures, premises or parts of the room (in compliance with designing order) where unique exhibits, materials, publications, handwritings, catalogues, descriptions, reviews and devices, as well as other especially valuable documents and information are located;

195.6. in fire compartments of the structure of type of use IV where there are spectator tribunes with at least 5000 seats, if there are premises under the tribune where the fire load is more than 300 MJ/m2;

195.7. in the structures of type of use IV where there is a stage with the flies, if in one fire compartment there are at least 800 seats or the area of the stage exceeds 120 m2, intending automatic firefighting sprinkler and drencher system in the premises of the stage compartment, stage and trap room;

195.8. in fire compartments of the structures of type of use VI where pumping, pouring, release, prepacking or storage of oil, oil products and other inflammable substances is intended and the area of which is more than 300 m2;

195.9. in the structures of type of use IV where the mark of floor level of the highest storey exceeds eight metres, in fire compartments the area of which is more than 5000 m2;

195.10. in fire compartments of the structures of type of use VII where placement of at least 25 vehicles with elevators and other vehicle conveyance devices is intended; and

195.11. in surface reservoirs of oil, oil products and other inflammable substances the capacity of which is more than 5000 m3.

196. Automatic firefighting systems need not be intended in open structures.

197. In the structures and premises where arrangement of another automatic fire protection system is intended, turning on of such systems in the automatic control mode shall be intended in compliance with regulatory enactments and designing order.

198. Automatic water cooling systems and automatic water curtain shall be intended for the protection of fire safety boundary structures and openings in compliance with regulatory enactments and designing order.

199. If water supply sources for firefighting needs cannot ensure the water pressure necessary for the operation of automatic firefighting systems, automatic firefighting water curtains and automatic cooling systems, at least two (working and emergency) independent firefighting pumps or pump groups shall be intended. Each pump or one pump group shall ensure the water pressure and flow necessary for firefighting needs. At least one pump or pump group in automatic firefighting systems must have an internal combustion engine or an electric generator with internal combustion engine shall be intended for power supply of firefighting pumps. Electric generator shall ensure power supply of firefighting pumps automatically, if the operation of power supply network is disturbed during the operation of pumps.

200. The structures and premises referred to in Sub-paragraphs 195.1, 195.2, 195.3, 195.4, 195.5, 195.7, 195.8 and 195.10 of this Construction Standard shall be equipped with automatic firefighting systems of water sprinkler or water drencher type (except the structures and premises where fire distinguishing with water will not be possible or inefficient and where an automatic firefighting system of another type, which will not reduce evacuation safety of persons, must be intended).

7.6. Requirements for Automatic Smoke Exhaust Systems and 
Automatic Air Overpressure Systems

7.6.1. General Requirements

201. At least 30 minutes of uninterrupted operation in case of fire shall be ensured for an automatic smoke exhaust system and an automatic air overpressure system, ensuring appropriate fire protection for power supply, control and monitor circuits of the systems.

202. Air suction devices of automatic air overpressure systems, smoke exhaust and compensating air suction devices of automatic smoke exhaust systems shall be designed so as the smoke to be discharged from the structure is not conveyed (recirculated) back to the burning structure and to adjacent structures.

7.6.2. Requirements for Automatic Air Overpressure Systems and 
Automatic Smoke Exhaust Systems

203. Automatic control from a signal generated by the following systems shall be intended for automatic air overpressure systems:

203.1. automatic fire detection and alarm systems;

203.2. automatic sprinkler firefighting systems;

203.3. manual remote control and distance control devices, which are arranged in the escape routes at the exits from premises, which are protected with this system, and in the premises where control and monitor panels of such systems are located.

204. Automatic control from a signal generated by the following systems shall be intended for automatic smoke exhaust systems:

204.1. automatic fire detection and alarm systems;

204.2. automatic sprinkler firefighting systems;

204.3. with manual remote control from distance control devices, which are arranged in the escape routes at the exits from premises, which are protected with this system, and in the premises where control and monitor panels of such systems are located.

205. Smoke dampers and smoke manholes of an automatic smoke exhaust system shall be intended in the upper part of the premises not lower than 80% of the height of the room.

206. Automatic apertures or openings for compensation air supply shall be intended in the lower part of the premises.

207. In the atria, which are higher than 24 metres, an automatic smoke exhaust system with mechanical traction or mechanical compensation air supply shall be intended.

8. Non-automatic Firefighting Systems

8.1. General Requirements

208. In compliance with the type of use of a structure or room and the layout of premises the following non-automatic fire protection systems shall be intended:

208.1. non-automatic firefighting systems;

208.2. non-automatic water cooling systems;

208.3. non-automatic firefighting water curtains;

208.4. non-automatic smoke exhaust systems.

209. Non-automatic firefighting systems may be replaced with an automatic firefighting system.

8.2. Requirements for Non-automatic Firefighting Systems, Non-automatic Water Cooling Systems and Non-automatic Water Firefighting Curtains

210. Non-automatic firefighting systems shall be intended:

210.1. in surface reservoirs of oil, oil products and other inflammable substances, the capacity of which is 3000-5000 m3;

210.2. in railway engineering structures (scaffold bridges) for pouring, filling and pumping of oil products and other inflammable substances, the length of which is more than 100 metres;

210.3. in technological yards of wharfs for tankers.

211. Non-automatic water cooling systems shall be intended in surface reservoirs for oil, oil products, gas and other inflammable substances, the walls of which is higher than 12 metres.

212. Non-automatic firefighting water curtain shall be intended in wharfs for tankers in order to prevent the flame spread between tankers and wharf.

213. Non-automatic firefighting systems, non-automatic water cooling systems and non-automatic firefighting water curtain shall be designed in compliance with regulatory enactments and designing order, intending manual control devices for turning on the operation of such system, which are located at the engineering structure to be protected or in the room where control and monitor panels of such system are located.

8.3. Requirements for Non-automatic Smoke Exhaust Systems

214. Manual remote control with distance control devices shall be intended for non-automatic smoke exhaust systems, which are arranged in the escape routes in each storey at the exits from premises, which are protected with this system, and in the premises where control and monitor panels of such systems are located.

215. It shall be intended that the duration of operation of non-automatic smoke exhaust systems in case of fire is at least 30 minutes, ensuring appropriate fire protection for power supply, control and monitor circuits of the system.

216. Smoke dampers, smoke manholes and other smoke exhaust apertures to be controlled, of a non-automatic smoke exhaust system, shall be intended in the upper part of the premises not lower than 80% of the height of the room. This requirement shall not apply to staircases.

217. Apertures or openings for compensation air supply of a non-automatic smoke exhaust system shall be intended in the lower part of the premises.

218. In the premises which are higher than 24 metres, a smoke exhaust system with mechanical traction or mechanical compensation air supply shall be intended.

9. Lightning Protection

219. Lightning protection systems shall be installed in order to prevent ignition of buildings and structures thereof in case of lightning discharge.

220. Level of lightning protection and necessity for the installation thereof shall be determined, taking into account the characteristics of the structure and the risk criteria.

221. Lightning protection shall be designed in compliance with the regulatory enactments regulating construction of internal wiring of buildings.

222. Installation of the lightning protection shall be mandatory for the structures with explosive environment.

Minister for Economics 		A. Kampars

Annex

to the Latvian Construction Standard LBN 201-10

“Fire Safety of Structures”

(approved with Cabinet Regulation

No. 498

of 28 June 2011)

#### Indicators of Fire Safety of Structures

Table 1

Fire Resistance of Building Structures of Structures

| No. | Building structure | Minimum fire resistance of building structures of structures depending on fire stability level of structures |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | U1 |  | U2 |  | U3 |
|  |  | U1a | U1b | U2a | U2b |  |
| 1. | Supporting walls and walls of the staircase | REI 120* | REI 60 | REI 60 | REI 30 | not standardised |
| 2. | Delimiting structure of another a room, separated by a fire-resistant structure***** | EI 60 | EI 30 | EI 60 | EI 30 | not standardised |
| 3. | Columns | REI 120* | R60** | R60 | R 30** | not standardised |
| 4. | Landings, beams, flights, steps | R 60 | R 30 | R 60 | R 30 | not standardised |
| 5. | Horizontal delimiting structure of the staircase | R 60 | R 30 | R 60 | R 30 | not standardised |
| 6. | Coverings including bays | REI 60 | REI 30 | REI 60 | REI 30 | not standardised |
| 7. | Flat roof*** | R 60 | R 30 | R 60 | R 30 | not standardised |
| 8. | Supporting building structures of the roof*** | R 30 | R 15 | R 15 | R 15 | not standardised |
| 9. | Fire-proof wall | REI 180-M | REI 120-M | REI 60-M | REI 60-M | REI 60-M |
| 10. | Delimiting structure of the fire compartment | REI 180 | REI 120 | REI 60 | REI 60 | REI 60-M |
| 11. | Doors, windows, gates, manholes and valves in fire walls and boundary structures of the fire compartment**** | EI 60 | EI 60 | EI 30 | EI 30 | EI 30 |
| 12. | Filling of openings in boundary structures of the a room, separated by a fire-resistant structure***** | EI 30 | EI 30 | EI 30 | EI 30 | not standardised |
| 13. | Doors of staircases***** | EI 30 | EI 30 | EI 30 | EI 30 | not standardised |
| 14. | Bearing structures of balcony, terrace, gallery | R 30 | R 15 | R 30 | R 15 | not standardised |

Notes.

1. * In the structures of type of use I of fire stability level U1a where the mark of floor level of the highest storey is from 50 to 75 metres, the fire resistance of supporting walls and walls and columns of staircases shall be at least REI 180.

2. ** In the structures of fireproofness one-storey U1b and U2b the minimum fire resistance of columns is not regulated, if the reaction to fire class of construction products is at least A2-s1,d0.

3. *** In the structures of fire stability level U1b and U2b where the mark of floor level of the highest storey is up to 8 metres, the minimum fire resistance of building structures of the flat roof is not regulated, if the reaction to fire class of construction products of the flat roof is at least A2-s1,d0.

4. **** In applying Sub-paragraph 52.2 of the Latvian Construction Standard LBN 201-10 “Fire Safety of Structures” (hereinafter – Construction Standard), the thermal insulation indicator I may be replaced with the heat radiation limitation indicator W.

5. The bearing structures of the roof are columns, frameworks, rafters and purlins; lathing is not bearing structure of the roof.

6. The fire resistance of non-protected steel structures, the thickness of wall of which is at least 0.8 mm, shall be R15.

7. ***** In applying Paragraph 49 of the Construction Standard, the thermal insulation indicator I may be replaced with the heat radiation limitation indicator W.

Table 2

#### Minimum Reaction to Fire Classes of Construction Products*

| No. | Building structures | Minimum reaction to fire classes of building products of building structures of structures depending on fire stability level of structures |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | U1 |  | U2 |  | U3 |
|  |  | U1a | U1b | U2a | U2b |  |
| 1. | Walls of the staircase | A1 | A1 | A1 | A1 | not standardised |
| 2. | Supporting walls and columns of frame | A1 | A1 | A2-s1,d0** | B-s2,d0 | not standardised |
| 3. | Landings, beams, flights, steps | A1 | A1 | A2-s1,d0 | A2-s1,d0 | not standardised |
| 4. | External walls | A2-s1,d0 | A2-s1,d0 | B-s1,d0 | not standardised | not standardised |
| 5. | Horizontal delimiting structure of the staircase | A1 | A1 | A2-s1,d0 | A2-s1,d0 | not standardised |
| 6. | Inter-storey coverings and flat roof | A1 | A2-s1,d0 | B-s1,d0*** | B-s2,d0*** | not standardised |
| 7. | Supporting building structure of the roof | A2-s1,d0 | A2-s1,d0 | not standardised | not standardised | not standardised |
| 8. | Fire-proof wall and delimiting structure of the fire compartment | A1 | A1 | A1 | A2-s1,d0 | A2-s1,d0 |
| 9. | Delimiting structure of the a room, separated by a fire-resistant structure | A2-s1,d0 | A2-s1,d0 | B-s1,d0 | B-s1,d0 | not intended |
| 10. | Doors, windows, gates, manholes and valves |  |  |  |  |  |
| 10.1. | in boundary structures of the fire compartment | A2-s1,d0 | A2-s1,d0 | A2-s1,d0 | A2-s1,d0 | A2-s1,d0 |
| 10.2. | delimiting structure of the a room, separated by a fire-resistant structure | B-s1,d0 | B-s1,d0 | B-s1,d0 | B-s1,d0 | not intended |
| 11. | Bearing structures of balcony and loggia, terrace and gallery | A2-s1,d0 | A2-s1,d0 | B-s1,d0*** | B-s1,d0*** | not standardised |

Notes.

1. * The requirements included in the Table shall apply to building structures, but shall not apply to the finishing.

2. ** In the structures of type of use V where the mark of floor level of the highest storey is from 8 to 14 metres, it is allowed to reduce the reaction to fire class of supporting walls and columns of frame up to B-s1,d0, if:

1) the possibility to evacuate is ensured for users of the structure through at least two separate emergency exits which are located in different places;

2) an openable opening is intended in each room where persons may stay permanently (Sub-chapter 3.3 of the Construction Standard), which is accessible by firefighting rescue equipment (vehicle with ladders);

3) all premises must be equipped with automatic firefighting systems (sprinklers).

3. *** It is allowed to use construction products, the reaction to fire class of which is lower than B-s1,d0, if the structure of the covering (flat roof) is protected with a construction product from the upper side, the reaction to fire class of which is at least A2-s1,d0.

Table 3

#### Maximum Area of Fire Compartment

| Type of use of the structure | Fire stability level | Mark of floor level of the highest storey of the structure (m) | Maximum area of fire compartment (m2) |
| --- | --- | --- | --- |
| I | U1a | over 28 | 2500 |
|  | U1a | up to 28 | 5000 |
|  | U1a | up to 8 | not limited |
|  | U1b | up to 8 | 5000 |
|  | U2a | up to 28 | 2500 |
|  | U2b | up to 8 | 2500 |
|  | U3 | up to 8 | 1600 |
| II, V | U1a | over 28 | 5000 |
|  | U1a | up to 28 | 10000 |
|  | U1a | up to 8 | 15000 |
|  | U1b | up to 8 | 5000 |
|  | U2a | up to 28 | 5000 |
|  | U2b | up to 8 | 2500 |
|  | U3 | up to 8 | 1600 |
| III, IVa | U1a | over 28 | 5000 |
|  | U1a | up to 28 | 10000 |
|  | U1a | up to 8 | 15000 |
|  | U1b | up to 8 | 5000 |
|  | U2a | up to 28 | 2500 |
|  | U2b | up to 8 | 1200 |
|  | U3 | up to 8 | 800 |
| IV | U1a | not limited | 10000 |
|  | U1b | up to 8 | 20000 |
|  | U2a | up to 28 | 5000 |
|  | U2b | up to 8 | 2500 |
|  | U3 | up to 8 | 1600 |
| VI, VII | U1a | not limited | not limited if the fire load is less than 600 MJ/m2 |
|  |  |  | 10000, if the fire load is from 600 to 1200 MJ/m2 (including) |
|  |  |  | 5000, if the fire load is over 1200 MJ/m2 |
|  | U1b | up to 8 | not limited if the fire load is less than 600 MJ/m2 |
|  |  |  | 10000, if the fire load is from 600 to 1200 MJ/m2 (including) |
|  |  |  | 5000, if the fire load is over 1200 MJ/m2 |
|  | U2a | up to 28 | 10000, if the fire load is less than 600 MJ/m2 |
|  |  |  | 5000, if the fire load is from 600 to 1200 MJ/m2 (including) |
|  |  |  | 2500, if the fire load is over 1200 MJ/m2 |
|  | U2b | up to 8 | 5000, if the fire load is less than 600 MJ/m2 |
|  |  |  | 2500, if the fire load is from 600 to 1200 MJ/m2 (including) |
|  |  |  | 1600, if the fire load is over 1200 MJ/m2 |
|  | U3 | up to 8 | 2000 |

Note. If an automatic firefighting system is arranged, the maximum area of fire compartment specified in this Table may be doubled.

Table 4

Comparison of Reaction to Fire Classes and Combustibility Groups

| No. | Reaction to fire class | Combustibility group in compliance with regulatory enactments |
| --- | --- | --- |
| 1. | A1, A1FL | non-combustible |
| 2. | A2-s1,d0 A2FL-s1 | hardly combustible |
| 3. | B-s1,d0 Bs2,d0; Bs2,d1; Bs2,d2 Bs3,d0; Bs3,d1; Bs3,d2 BFL-s1; BROOF(t1) | hardly combustible |
| 4. | C-s2, d1; CFL-s1 D-s2, d2; DFL-s1 D-s1; E; E-d2; F EFL; FFL; FROOF(t1) | combustible |

Table 5

Requirements for Heat Insulation Systems and Materials of External Walls

| Fire stability level of the structure | Mark of floor level of the highest storey of the structure (m) |  | Minimum reaction to fire class of construction products |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | non-ventilating facades |  |  | ventilating facades |  |
|  |  |  | heat insulation | external finishing | heat insulation system with external finishing* | heat insulation | external finishing |
| U1 |  |  | A2-s1,d0 | A2-s1,d0 | A2-s1,d0 | A2-s1,d0 | A2-s1,d0 |
|  | U1b to 8 (including) |  | B-s1,d0 | A2-s1,d0 | B-s1,d0 | A2-s1,d0 | B-s1,d0** |
| U2 | to 28 (including) | variant A | B-s1,d0 or E-d2 with delimiting zones*** | A2-s1,d0 | B-s1,d0 or C-s2,d2 with delimiting zones*** | A2-s1,d0 or B-s1,d0 with delimiting zones*** | B-s1,d0*** |
|  |  | variant B | A2-s1,d0 | B-s1,d0 |  |  |  |
|  | to 8 (including) | variant A | C-s2,d1 or E-d2 with delimiting zones*** | A2-s1,d0 | D-s2,d2 | B-s1,d0 | D-s2,d0 |
|  |  | variant B | B-s1,d0 | C-s2,d2 |  |  |  |
| U3 | to 8 (including) |  | not standardised | not standardised | not standardised | not standardised | not standardised |

Notes.

1. * Heat insulation system is a multi-layer external heat insulation which is confirmed in accordance with the procedures specified in the Law On Conformity Assessment.

2. ** It is allowed to use construction products of the reaction to fire class Bs1,d0, the maximum area of which in one plane does not exceed 200 m2 of the total surface and which is horizontally delimited with zones of construction products of the reaction to fire class at least A2-sl,d0 on the level of inter-storey coverings.

3. *** Fire-proof delimiting zones/barriers shall be placed on the level inter-storey covering forming fire compartment, but not less than every two storeys. The minimum height of the fire-proof zone shall be 200 mm on the facade, thickness shall be the thickness of the heat insulation layer, it shall be made of construction products of the reaction to fire class A2-s1,d0 (including finishing).

4. Requirements for the reaction to fire class for heat insulation and external finishing of non-ventilating facades of the structures of fire stability levels U2 are possible in two variants – depending on structure of multi-layer heat insulation.

5. Reaction to fire class for the bearing structure (frame) of the structures of fire stability level U2, to which external heat insulation structures are attached, shall at least C-s2,d1.

6. In the structures of fire stability level U2 where the mark of floor level of the highest storey is up to 14 metres, it is allowed to make the bearing structure (frame) of the external finishing from the construction products, the reaction to fire class of which is at least D-s2,d2, if the construction products, the reaction to fire class of which is at least A2-s1,d0, have been used for heat insulation.

7. In the structures of fire stability level U1 and in the structures of fire stability level U2 where the mark of floor level of the highest storey is above 8 metres, it is allowed to use construction products of external heat insulation, the reaction to fire class of which is lower than B-s1,d0, on the base, the reaction to fire class of which is at least A2-s1,d0.

Table 6

Maximum Length of Escape Route and Area of Room per One User

| No. | Type of use of the structure | Maximum distance to the nearest emergency exit (m) | Maximum distance between emergency exits | Area of room (m2) to be calculated per one user |
| --- | --- | --- | --- | --- |
| 1. | type of use I: |  |  |  |
| 1.1. | one emergency exit | 30 | - | 10 |
| 1.2. | two or several emergency exits | 45 | 90 | 10 |
| 2. | type of use II | 30 | 60 | 10 |
| 3. | type of use III | 30 | 60 | 10 |
| 4. | type of use IV: |  |  |  |
| 4.1. | trade premises | 45 | 90 | 3* |
| 4.2. | premises for recreation and public measures | 45 | 90 | 1.0 – in halls without seats or in compliance with the number of seats intended in the designing order |
| 4.3. | in structures of other types of use IV | 45 | 90 | in compliance with the number of seats intended in the designing order |
| 4.4. | type of use IVa | 30 | 60 | in compliance with the number of seats intended in the designing order |
| 5. | type of use V | 45 | 90 | 10 |
| 6. | types of use VI and VII** | 90 | 180 | in compliance with conditions of the technological process |

Notes.

1. * The area which is not occupied by trade and technological equipment shall be taken into account for the calculation.

2. ** In structures of types of use VI and VII with explosion hazard or fire load over 1200 MJ/m2 the maximum distance to the emergency exit shall be reduced for a half.

Table 7

Minimum Fire Safety Intervals between Structures

| Fire stability level of structures | Fire stability level of structures |  |  |
| --- | --- | --- | --- |
|  | U1 | U2 | U3 |
| U1 | 6 m | 7 m | 8 m |
| U2 | 7 m | 8 m | 9 m |
| U3 | 8 m | 9 m | 10 m |

Note. Distance between external walls or other boundary structures shall be regarded as the distance between buildings. If the structures of external walls of buildings have protrusions which are larger than 1 m, the distance from these structures shall be regarded as the fire safety distance.

Minister for Economics 		A. Kampars